## README
SPECTRE-1 SCRATCH STORAGE — PRICING & COMPLIANCE MATRIX
ORNL / UT-Battelle, LLC · Attachment C Technical Requirements v0.4 (May 2026) · Bldg 5300 DC-1N
HOW TO USE THIS WORKBOOK
Yellow cells | Fill these in. Everything else is a formula, a label, or a pre-populated requirement — do not overwrite.
Blue text | A hardcoded input you entered.
Black text | A formula. It recalculates from your inputs.
Grey italic row | Example row showing the expected format. Delete or overwrite before submission.
WHAT THE RFP ASKS FOR
§1 Pricing breakouts | "Pricing breakouts for all offered node types and relevant components." Use the 'Node & SSU Pricing' tab.
§1 Three media options | All-HDD, all-Flash, and hybrid must each be priced. Tag every line with its Config on the pricing tabs.
§1 Adapter choice | Price each high-speed network adapter option separately — see 'Network Adapters'.
§1 Media capacity choice | Price each drive capacity/technology option separately — see 'Media Options'.
§1 Lead times | The RFP explicitly wants part lead times so ORNL can trade scope against schedule. Fill the lead-time columns everywhere and summarize on 'Lead Time & Risk'.
§3 Unmet requirements | Any requirement not met must be identified with a discrepancy description, justification, and mitigation. Use the 'Compliance Matrix' tab.
§3.2 50% floorspace | The base bid occupies 8 of 16 production racks. Remaining footprint is priced as SSU growth options.
§5 Support | Four-year base, with separately priced 5th-year, 6th-year, and deferred-maintenance options — 'Support & Maintenance' tab.
§5.5 Analyst | The on-site System Software Analyst is separately priced and requires a DOE Q-clearance.
HARD CONSTRAINTS TO CHECK EVERY LINE AGAINST
Recording technology | §3.2 bars HAMR, MAMR, and SMR. PMR/CMR only. Largest compliant drive is ~26 TB. Any HAMR/SMR line is non-compliant.
FIPS SED on all media | §3.2 requires FIPS 140-2 certified OR FIPS 140-3 compliant self-encrypting drives for ALL storage media, flash and disk.
Power per rack | 60 A / 208 VAC 3-phase = 17.3 kW usable per feed. Dual-fed diverse, so design to survive on ONE side: 17.3 kW/rack.
Total power | 275 kW cap across production + cluster management + 5300-DC TDS. The 8-rack base bid budget is ~138 kW.
Rack envelope | 17 racks total (16 production + 1 TDS), 600 mm wide, 50U usable. Extra-deep (1300 mm) cabinets permitted.
TAA | §3.1.6 requires TAA compliance on all hardware and software. HDD and NAND country-of-origin is the hard part — verify per part number.
Uniform DIMMs | §3.2 requires ECC DIMMs of a uniform FRU type across the system. One DIMM part number everywhere.
Minimize node types | §5.2 requires hot spare NODES of each type in the parts cache. Every additional node type multiplies spares cost.
TABS
Config Summary | Roll-up of the three media configurations. Pulls from the pricing tabs — check it after every edit.
Node & SSU Pricing | Line-item pricing for every node and SSU type, tagged by config, with U, watts, lead time, TAA, FIPS.
Media Options | Drive-by-drive options. Includes the recording-technology and FIPS/TAA compliance gates.
Network Adapters | 400 GbE / Slingshot / InfiniBand / Ultra Ethernet options.
TDS Pricing | Per-TDS build. Two identical systems required (§3.2.1).
Support & Maintenance | Years 1-4 base plus 5th/6th year and deferred options. Quoted by the OEM per §5.
Services & Deliverables | Install, RDHX, and the full ATO/SCRM documentation package. Price these — do not absorb them.
Lead Time & Risk | Long-lead components and alternative delivery schedules per §1 and PPI §2.3.
Compliance Matrix | Pre-populated with the RFP's requirements. Mark Comply / Exception / Alternative on every row.
Prepared for internal capture use. Verify every part number, FIPS status, and country of origin with the OEM before submission.

## Config Summary
CONFIG SUMMARY — three media strategies
Capacity, power and price roll-up. Yellow cells are direct inputs; the rest pull from the pricing tabs.
Metric | Unit | All-HDD | All-Flash | Hybrid (recommended) | Constraint / target | Pass?
Usable capacity | PB |  |  |  | 150–250 PB (§3.2.2) — confirm 8-rack vs 16-rack
Raw capacity | PB |  |  |  | —
Erasure coding scheme | text |  |  |  | e.g. 8+2 declustered
Storage efficiency | % |  |  |  | usable ÷ raw
Production racks used | count |  |  |  | 8 of 16 for base bid (§3.2)
Rack U consumed | U |  |  |  | ≤ 50U per rack (§7)
Total power draw | kW |  |  |  | ≤ 138 kW for 8-rack base; ≤ 275 kW all-in (§7.1)
Power per rack | kW |  |  |  | ≤ 17.3 kW on a single feed (§7.1)
HSN endpoints | count |  |  |  | ≤ 120 (§3.2.2)
Aggregate read bandwidth | GB/s |  |  |  | Offeror-stated, aged (§4, §4.2)
Aggregate write bandwidth | GB/s |  |  |  | Offeror-stated, aged (§4, §4.2)
Namespace IOPS (4 KiB) | M IOPS |  |  |  | Offeror-stated, aged (§4)
mdtest file create rate | K ops/s |  |  |  | At 70% aged utilization (§4.2)
Total inodes supported | billions |  |  |  | Plan for 10B (see brief §3.4)
PRICE ROLL-UP
Hardware subcontract — base bid (8 racks)
Hardware subcontract — SSU growth options (racks 9–16)
TDS — 2 systems
Services & deliverables (separately priced)
Support & maintenance — years 1–4
Support & maintenance — year 5 option
Support & maintenance — year 6 option
On-site System Software Analyst (Q-cleared), 4 yr
TOTAL EVALUATED PRICE
$ per usable PB (hardware only)
Note: 'usable' must be defined in the proposal — post-erasure-code, post-filesystem-overhead, and before the 70% aged-utilization test of §4.2. Confirm whether ORNL's PB means 10^15 or PiB (2^50); the difference is 12.6%.

## Node & SSU Pricing
NODE & SSU PRICING
§1: pricing breakouts for all offered node types and relevant components. Tag every line with the config it belongs to.
ID | Config | Node / SSU type | Description | Mfr part no. | Qty | U each | Watts each | Unit price | Extended price | Total U | Total kW | Lead time (wks) | TAA country of origin | FIPS status | Notes
EX | Hybrid | Capacity SSU | 4U102 JBOD, 102 x 26TB CMR SED | 1EX2000-EXAMPLE | 60 | 4 | 1300 | 185000 |  |  |  | 26 | Thailand — verify | 140-3 compliant SED | Example row — overwrite
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
41
42
43
44
45
46
47
48
49
50
51
52
53
54
55
TOTAL
Config values must be exactly: All-HDD, All-Flash, Hybrid, or All (for components common to every configuration). Config Summary sums on these strings.
Every distinct node type here drives a hot-spare node in the §5.2 parts cache. Consolidating node types lowers both spares cost and TDS cost.

## Media Options
MEDIA OPTIONS
§1 invites alternative HDD and flash technologies with lead times. §3.2 bars HAMR, MAMR and SMR, and requires FIPS SEDs on all media.
ID | Media type | Mfr / model | Part no. | Capacity (TB) | Recording tech | Interface | SED? | FIPS status | Country of origin | TAA compliant? | Watts (typ) | Unit price | $ per TB | Lead time (wks) | Endurance (DWPD) | Compliant? | Notes
EX | HDD | WD Ultrastar DC HC590 | WUH722626AL5201 | 26 | ePMR / CMR | SAS | Y | 140-3 compliant | Thailand | Verify | 9 | 620 |  | 26 | n/a |  | Example row — overwrite. Largest CMR-compliant capacity available.
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
Recording tech must read PMR or CMR for HDDs. The Compliant? column flags HAMR / MAMR / SMR automatically, per §3.2.
FIPS status: enter '140-2 certified', '140-3 validated', '140-3 compliant', or 'none'. §3.2 accepts 140-2 certified OR 140-3 compliant SEDs. Note FIPS 140-2 certificates moved to historical status in 2026 — confirm ORNL still accepts them.
Country of origin drives TAA (§3.1.6). HDD and NAND assembly frequently occurs in non-TAA-designated countries. Get a written country-of-origin statement per part number — do not assume.
Endurance matters: scratch is write-heavy and churny. Confirm QLC DWPD covers the projected daily scratch turnover for the full 4–6 year PoP, or use TLC on the write-intensive tier.

## Network Adapters
NETWORK ADAPTER OPTIONS
§1: 'Choice of network adapter.' §3.2 permits 400 GbE or equivalent — Ultra Ethernet, Slingshot, or InfiniBand.
ID | Fabric | Mfr / model | Part no. | Ports/adapter | Speed per port | Watts each | Unit price | Qty | Extended price | Lead time (wks) | TAA origin | Notes
EX | 400 GbE | Example NIC | PN-EXAMPLE | 2 | 400 Gb/s | 75 | 3200 | 30 |  | 20 | Israel | Example row — overwrite
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
TOTAL
Slingshot is HPE-proprietary. If SPECTRE-1's compute fabric is Slingshot, confirm third-party NIC availability and licensing before quoting a non-HPE storage platform against it.
Ultra Ethernet silicon is early in 2026–27. If quoting UE, state firmware maturity and interoperability test evidence, and offer 400 GbE as the low-risk alternate.
Endpoint count is capped at 120 (§3.2.2) but power caps it lower in practice — each 400G server costs roughly 1.1–1.2 kW against a ~138 kW base-bid budget.

## TDS Pricing
TEST & DEVELOPMENT SYSTEMS
§3.2.1: two identical TDS, each a fully functional standalone system with a minimal set of every component in the production design.
ID | Component | Description | Qty per TDS | Unit price | Extended per TDS | No. of TDS | Total | Lead time (wks) | Notes
1 | Metadata / management server |  |  |  |  | 2
2 | Flash SSU (minimum viable) |  |  |  |  | 2
3 | HDD SSU (minimum viable, hybrid only) |  |  |  |  | 2
4 | Provisioning / cluster management server |  |  |  |  | 2
5 | High-speed network adapters |  |  |  |  | 2
6 | Top-of-rack management switching |  |  |  |  | 2
7 | Cabinet, PDUs, rails |  |  |  |  | 2
8 | Rear Door Heat Exchanger |  |  |  |  | 2
9 | File system + HA + RHEL licensing |  |  |  |  | 2
10 | Installation & integration |  |  |  |  | 2
11 | Cabling & optics |  |  |  |  | 2
TOTAL — BOTH TDS
One TDS occupies the 17th rack at 5300-DC and counts against the 275 kW cap. The second TDS location is not stated in Attachment C — submit a clarification question before pricing site work for it.
§3.2.1: TDS support co-terminates with the production COMPUTE partition, not with this storage contract. Confirm that end date before pricing the support line.
§5.2: TDS hardware may NOT be used as the spare parts cache. Price spares separately.

## Support & Maintenance
SUPPORT & MAINTENANCE
§5 — quoted by the OEM. Four-year base with separately priced 5th-year, 6th-year and deferred-maintenance options.
ID | Item | RFP ref | Year 1 | Year 2 | Year 3 | Year 4 | Yr 5 (option) | Yr 6 (option) | Total
1 | Hardware maintenance — production system | §5
2 | Hardware maintenance — TDS (x2) | §3.2.1
3 | File system software licensing & support | §5.4
4 | High-availability (HA) licensing | §5.4
5 | RHEL licensing & support | §5
6 | Quarterly system updates & security patching | §5
7 | Critical/High CVSS v4 remediation within 30 days | §3.1.8
8 | Remote technical support | §5
9 | On-site technical support | §5
10 | On-site parts cache — initial stocking | §5.2
11 | On-site parts cache — refresh | §5.2
12 | Hardware retention / no-return service (all FRUs) | §5.3
13 | Performance optimization & monitoring services | §5
14 | On-site System Software Analyst (DOE Q-cleared) | §5.5
Deferred maintenance option (§5.1) — describe & price
TOTALS
§5.1: years 5 and 6 must be priced at the standard four-year rate.
§5.1: the maintenance period begins upon successful Acceptance (Q2CY2027), but the draft subcontract PoP starts 12/15/2026. Submit a clarification question and price to the answer.
§5.3: no hardware leaves the site — ORNL destroys it. Every FRU needs a retention/no-return service, and you get no failure-analysis feedback, so size the parts cache conservatively.
§5.2: the cache must sustain all repair actions for two weeks with no refresh, and must include hot spare NODES of every proposed type.
§3.1.8 is a contractual SLA on third-party dependencies, not just your own code. In an air-gapped classified enclave, a 30-day patch cycle needs a defined media-transfer process — price the labor.

## Services & Deliverables
SERVICES & DELIVERABLES
The documentation and services package. Price these explicitly — the ATO and SCRM artifacts alone are hundreds of hours.
ID | Deliverable | RFP ref | In hardware price? | Separately priced | Est. hours | Owner | Notes
1 | Site Preparation Plan (within 30 days of award) | §8.3
2 | Maintenance & Support Plan (30 days before first delivery) | §8.4
3 | Proposed delivery / installation / acceptance schedule | §8.2
4 | Executive Liaison & Technical Project Manager assignment | §8.2
5 | Delivery, uncrating, inspection, staging, mounting, packaging removal | §6, §7.2
6 | RDHX supply, delivery, mounting, hose & control valve connection | §7.2
7 | Cable management — overhead electrical to equipment | §7.1
8 | Cable management — cabinet-to-cabinet network (optical/STP) | §3.1.4, §7.1
9 | Security Control Implementation Statements — all 800-53 High controls | §3.1.13
10 | System Security Plan (asset inventory, boundaries, network diagrams) | §3.1.13
11 | Configuration Management Plan | §3.1.13
12 | Incident Response Plan | §3.1.13
13 | SCRM Policy and SOP | §3.1.9
14 | Supplier Risk Register and Scorecards | §3.1.9
15 | Component Authenticity Logs & Firmware Integrity Scans | §3.1.9
16 | SDLC checklists & secure configuration baselines | §3.1.12
17 | Sample SOWs including cyber clauses | §3.1.12
18 | STIG & SCAP scans on all nodes and network equipment + reports | §3.1.14
19 | Audit logging validation (AU control family) | §3.1.14
20 | Recommended testing procedures for the Company | §3.1.14
21 | Acceptance test support — IOR, mdtest, injected failures, stability | §4.2, §8.5
22 | Aged-namespace (70%) benchmark characterization | §4.2
23 | Interface documentation, procedures & drawings | §5.6
24 | Activity Hazard Analysis (AHA) | Attach. F
TOTAL
The RDHX scope (§7.2) is a mechanical contractor's work, not a storage OEM's. Identify the partner and price it before bid, including BACnet/IP integration and leak-detection commissioning.

## Lead Time & Risk
LEAD TIME & SCHEDULE RISK
§1 invites alternative delivery schedules to mitigate long-lead risk. PPI §2.3 governs. Delivery Q1CY2027 / Acceptance Q2CY2027.
ID | Component | Configs affected | Quoted lead time (wks) | Risk (H/M/L) | Driver | Mitigation / alternative schedule | Notes
1 | Nearline CMR HDDs (24–26 TB) | All-HDD, Hybrid |  |  | Nearline capacity heavily booked through 2026; CMR SKUs are a shrinking share of production as vendors shift to HAMR/SMR
2 | High-capacity QLC NAND | All-Flash, Hybrid |  |  | NAND allocation and pricing pressure through 2026; the RFP itself cites long lead times for memory technologies
3 | FIPS SED variants of top-capacity drives | All |  |  | SED/FIPS SKUs historically trail the leading capacity by a generation
4 | DRAM (uniform ECC DIMM FRU) | All |  |  | Memory market conditions cited in §1
5 | 400G NICs / Slingshot adapters | All |  |  | Fabric choice may be gated on the SPECTRE-1 compute award
6 | Ultra Ethernet silicon | All |  |  | Early-generation availability and firmware maturity in 2026–27
7 | Storage controllers / server platforms | All |  |  | Platform generation transition
8 | Cabinets, PDUs (port-switchable, locking, watertight) | All |  |  | Non-standard PDU spec per §7.1
9 | Rear Door Heat Exchangers | All |  |  | Custom spec: 1in sanitary, BACnet/IP, leak detect w/ shutdown, fail-closed
10 | Optical cable & transceivers (inter-cabinet) | All |  |  | §3.1.4 forbids passive copper DAC between cabinets
§1: 'Offerors can also propose alternative system delivery schedules to mitigate schedule risks.' A phased delivery — metadata and flash tier first, capacity tier second — protects the Q2CY2027 acceptance date and is worth offering explicitly.

## Compliance Matrix
COMPLIANCE MATRIX
§3: any requirement not met must be identified with a discrepancy description, justification, and proposed mitigation or alternative.
RFP § | Requirement | Comply / Exception / Alternative | Evidence or reference | Discrepancy & justification (required if Exception) | Proposed mitigation / alternative | Owner | Status
3.1.1 | NIST SP 800-53 Rev 5 High baseline, tailored for DoW systems
3.1.1 | NIST SP 800-223 (HPC Security)
3.1.1 | NIST SP 800-207 (Zero Trust Architecture)
3.1.1 | NIST SP 800-216 (Vulnerability Disclosure)
3.1.1 | NIST SP 800-193 (Platform Firmware Resiliency)
3.1.1 | NIST SP 800-161 (Cybersecurity Supply Chain Risk)
3.1.1 | FIPS 140-3 and SP 800-52 / 800-57 / 800-131A for cryptography
3.1.2 | Data encrypted at rest
3.1.3 | Data encrypted in transit where technically feasible; describe exceptions
3.1.4 | All inter-cabinet cables optical or shielded twisted pair; intra-node optical preferred
3.1.5 | FIPS 140-3 compliant and/or NSA-approved cryptographic algorithms
3.1.6 | TAA compliance — all hardware, software and integrated components (19 U.S.C. 2501–2581)
3.1.7 | System capable of full ATO under RMF once transitioned to DoW; supply all supporting artifacts
3.1.8 | Active software support for full operational lifetime; Critical/High CVSS v4 fixes within 30 days
3.1.9 | SCRM strategy aligned to NIST SE-1 through SE-3, with register, scorecards and authenticity logs
3.1.10 | Secure boot and firmware controls; DISA STIG and SCAP compatibility; secure OS/hypervisor config
3.1.11 | All personnel — staff, vendors and subcontractors — are US citizens
3.1.12 | Formal secure SDLC with security checkpoints; version control, RBAC, audit trails
3.1.13 | SCIS, SSP, CM Plan, IR Plan delivered at system delivery
3.1.14 | Pre-handoff audit: STIG/SCAP scans, AU-family logging validation, test procedures
3.2 | SSU modular building blocks
3.2 | Highly available: redundant chassis components, power and software
3.2 | ECC DIMMs of a uniform FRU type
3.2 | HSN integration — 400 GbE or equivalent (UE, Slingshot, InfiniBand)
3.2 | PMR/CMR HDDs only — HAMR, MAMR and Shingled not permitted
3.2 | FIPS 140-2 certified or 140-3 compliant self-encrypting drives on all storage media
3.2 | Hot-swappable media, fans and power supplies where feasible
3.2 | Base proposal occupies 50% of production floorspace; remainder priced as SSU options
3.2.1 | Two identical Test & Development Systems, each fully functional and standalone
3.2.2 | Single POSIX-compliant namespace
3.2.2 | Up to 120 network endpoints to the compute-fabric HSN
3.2.2 | Between 150 PB and 250 PB usable space
3.2.3 | Data path and control plane do not require container orchestrators (preference)
4 | Namespace, per-SSU and per-component bandwidth, IOPS and latency; block and client level
4 | Complete test parameters, configurations and methodologies disclosed
4.2 | Acceptance against a namespace artificially aged to ~70% utilization
4.2 | End-to-end network bandwidth testing
4.2 | IOR and mdtest compared against published specifications
4.2 | Redundancy, fault tolerance and peripheral/torque validation
5 | Quarterly system updates and security patches at minimum
5.1 | Four-year maintenance base, with 5th-year, 6th-year and deferred options
5.2 | On-site parts cache sustaining two weeks of repairs with no refresh, incl. hot spare nodes
5.3 | No hardware leaves the site — destroyed by the Company
5.4 | All licenses provided: RHEL, file system, and HA functionality
5.5 | On-site System Software Analyst with DOE Q-clearance, separately priced
5.6 | Interface documentation, procedures and drawings
6 | Delivery, installation and integration; handling and disposition of all materials
7 | 17 x 600 mm racks (16 production + 1 TDS), 50U, overhead connectivity only, no raised floor
7 | Cluster management and 5300-DC TDS in separate cabinets within the space limit
7.1 | 3-phase 60 A 208 VAC IEC60309, dual-fed diverse (utility + UPS)
7.1 | Non-pocket in-rack PDUs: port-switchable, monitorable, watertight sleeve, outlet locking
7.1 | Total power not to exceed 275 kW
7.2 | RDHX per cabinet: top-fed, fail-closed valves, 1in sanitary connections
7.2 | RDHX flow <= 11 gpm each, supply water 60–68 F, room neutral at 75 F rack inlet
7.2 | BACnet/IP monitoring; rack-level leak detection with shut-down capability
7.2 | Check valve on return, control valve on supply; <5% parasitic heat during maintenance
7.2 | Offeror delivers, uncrates, stages, mounts and connects RDHXs and removes packaging
8.2 | Executive Liaison and Technical Project Manager identified
8.2 | Delivery/installation/integration/acceptance schedule aligned to §1 milestones
8.3 | Site Preparation Plan within 30 days of award
8.4 | Maintenance & Support Plan at least 30 days before first delivery
8.5 | Acceptance: hardware phase, functionality walk-through, performance test, stability test
8.5 | Benchmarks executable from a non-privileged account
Enter exactly 'Comply', 'Exception', or 'Alternative' in column C. §3 requires that every Exception carry a discrepancy description, a justification, and a proposed mitigation or alternative — columns E and F are mandatory for those rows.